## Checkout & Commissioning Sheet
Note Sheets for AFMS Checkout and Commissioning
Point-to-Point Checkout Tasks (do in order): | Value/Reading | Completed Y/N
Verify correct Base App is set for the installation (Restore)
Set Control Mode to DMPR POSITION CTRL (MSV4)
Verify all pressure transducers are set to voltage output and unipolar
Make zero adjustment to all pressure transducers
5901 AFMS only: Set the SA DP Range (AV95)
Pressure Assist only: Set the PA DP Range (AV96)
Set Supply Air Area (AV5) (square feet at sensing location)
Pressure Assist only: Inspect PA pickups are installed per installation guide
Calibrate Supply Air Flow (AV6 or AV7) (may need a balancer)
Pressure Assist only: Calibrate OAD/RAD Diff. Pressure offset (AV52) (may need a balancer)
Verify and calibrate Outside Air Temp using Offset (AV18) (very important)
Verify and calibrate Return Air Temp using Offset (AV19) (very important)
Verify and calibrate Mixed Air Temp using Offset (AV20) (very important)
Damper Span Calibration Tasks (do in order after point-to-point checkout): | Value/Reading | Completed Y/N
Set damper Stroke Time (AV45) (longest actuator run time to move damper from fully closed to open)
Set damper Actuator Voltage span (BV6)
Enable Learn Damper Span (BV3) (3-5 minutes to complete)
Verify Damper Span Learned (BV9)
Stroke damper and visibly verify positions at 0%, 50%, and 100% (AV9)
If damper actuator action is reverse (10v=closed), set Damper Reverse Action (BV4) to REVERSE
Record Minimum Inclinometer Value (AV47) (if using KMC Connect)
Record Maximum Inclinometer Value (AV48) (if using KMC Connect)
Stroke damper and verify that the reported Damper Position follows
If reported Damper Position is opposite of Damper Setpoint, set Inclinometer Action (BV10) to REVERSE
Learning Mode Tasks (do in order after damper span calibration): | Value/Reading | Completed Y/N
Verify current Outside Air Return Air Delta Temp (AV11) is greater than Min Delta Temp (AV12) for Learning Mode
Ensure that Min Delta Temp (AV12) will be maintained throughout the entire learn process (approx. 2hrs) (Time Between Samples [AV36] * 9 [samples per position] * 13 positions)
Ensure no damage can be done by keeping OA damper open for extended period (e.g. freeze stat, freeze coils, etc.)
If Learn Ready (BV1) = READY then enable Learning Mode (BV2). Otherwise, set Auto Learn Enable (BV8) to ON; learning mode will then start when ready.
Verify AFMS Status (MSV2) is in LEARN MODE.
Verify Learning Mode completed: record Date of Last Learn (YYMMDD) (AV39)
Record AFMS Table data using AFMS Post Table or AFMS PA Post Table
Set Control Mode (MSV4) to what will be the normal mode
For hardwired outputs, set Flows_at_10VDC (AV44) to 10 volts (requires software if changing from default)
Firmware Version: R1.7.0.9 |  | Doc Rev Date: 01 December 2024

## AFMS Post Table
Standard AFMS Post Table
Standard AFMS | AV Input | Value
OAD CLOSED | AV21
OAD 0-5 Percent Open | AV22
OAD 5-10 Percent Open | AV23
OAD 10-15 Percent Open | AV24
OAD 15-20 Percent Open | AV25
OAD 20-30 Percent Open | AV26
OAD 30-40 Percent Open | AV27
OAD 40-50 Percent Open | AV28
OAD 50-60 Percent Open | AV29
OAD 60-70 Percent Open | AV30
OAD 70-80 Percent Open | AV31
OAD 80-90 Percent Open | AV32
OAD 90-100 Percent Open | AV33

## AFMS PA Post Table
Pressure Assist AFMS Post Table
PA AFMS | AV Input | Value
OAD Differential Closed | AV53
OAD Differential 5% Open | AV54
OAD Differential 10% Open | AV55
OAD Differential 15% Open | AV56
OAD Differential 20% Open | AV57
OAD Differential 30% Open | AV58
OAD Differential 40% Open | AV59
OAD Differential 50% Open | AV60
OAD Differential 60% Open | AV61
OAD Differential 70% Open | AV62
OAD Differential 80% Open | AV63
OAD Differential 90% Open | AV64
OAD Differential 100% Open | AV65
SA Flow Closed | AV67
SA Flow 5% Open | AV68
SA Flow 10% Open | AV69
SA Flow 15% Open | AV70
SA Flow 20% Open | AV71
SA Flow 30% Open | AV72
SA Flow 40% Open | AV73
SA Flow 50% Open | AV74
SA Flow 60% Open | AV75
SA Flow 70% Open | AV76
SA Flow 80% Open | AV77
SA Flow 90% Open | AV78
SA Flow 100% Open | AV79

## Free Area Calc
Fan Inlet or Round Duct
Inlet Size in Inches | 12
Number of Inlests | 9
Free Area | 7.0686
Square or Retangular Duct
Height In Inches | 12
Width In Inches | 12
Free Area | 1
Velocity to CFM Calc.
Velocity DP | 0.5
Free Area | 7.07
CFM | 20021.976
CFM to DP
CFM | 20022
Free Area | 7.07
DP | 0.5